[image: image1.png]


       [image: image2.png]


          [image: image3.png]




ENGINEERING SPECIFICATION

SYMCOM MODELS 201-100-SLD, 201-200-SLD 
SEAL LEAK DETECTOR
PART 1 GENERAL

PART 1 REFERENCES

PART 1 UL 508 Industrial Control Equipment – Underwriters Laboratories
PART 1 IEC 60947 Low Voltage Switchgear and Controlgear – International Electrotechnical Commission
PART 1 ANSI/IEEE C62.41 – American National Standards Institute/Institute of Electrical & Electronics Engineers 

PART 1 CSA C22.2 No. 14 Industrial Control Equipment – Canadian Standards Association
PART 1 WARRANTY

PART 1 Manufacturer Warranty:  The manufacturer shall guarantee the equipment to be free from material and workmanship defects


for a period of five years from the date of manufacture when installed and operated according to the manufacturer’s requirements.  
PART 2 PRODUCTS

PART 2 MANUFACTURERS

For the 201-100-SLD

The equipment specified shall be the 201-100-SLD, manufactured by SymCom, Inc.
For the 201-200-SLD

The equipment specified shall be the 201-200-SLD, manufactured by SymCom, Inc.

PART 2 DESCRIPTION

PART 2 Regulatory Requirements:

PART 2 The equipment shall be UL Listed as type NKCR—Industrial Control Equipment-Motor Controllers-Auxiliary Devices.

PART 2 The equipment shall be ULC Listed as type NKCR7—Industrial Control Equipment-Motor Controllers-Auxiliary Devices Certified for Canada.
PART 2 The equipment shall be CE marked for use in the European Union and evaluated against IEC 60947 Low Voltage Switchgear and Controlgear.

PART 2 Performance/Design Criteria:  SEAL LEAK DETECTOR
PART 2 Protective Leak Detection Functions:
PART 2 The equipment shall provide notification of the following conditions:

PART 2 Reduced resistance of the probe indicating a possible seal leak

PART 2 Capabilities and Features

PART 2 Inputs:
PART 2 The equipment shall provide one control input.
For the 201-100-SLD

PART 2 The equipment shall accept single-phase input voltage rated 95-120VAC.

For the 201-200-SLD

PART 2 The equipment shall accept single-phase input voltage rated 190-240VAC.

PART 2 Outputs:  

PART 2 The equipment shall include one Form C output relay contact pilot duty rated 480VA @ 240VAC.

PART 2 The equipment shall include one Form C output relay contact general purpose rated 10A @ 240VAC.
PART 2 Functional Specifications

PART 2 The equipment shall include a dial adjustment to set the input sensitivity from 4.7k to 100k ohms.

PART 2 The equipment shall have one indicator LED capable of indicating the status of the output relay.
PART 2 Electromagnetic Compatibility

PART 2 The equipment shall be immune to electrostatic discharge per IEC 61000-4-2, Level 3, 6kV contact discharge and 8kV air discharge.

PART 2 The equipment shall be immune to electrical fast transient bursts exceeding IEC 61000-4-4, Level 4.  Specified limits shall be 4kV.

PART 2 The equipment shall be immune to electrical surges per IEC 61000-4-5, Level 4.  Specified limits shall be Level 4, 4kV line-to-line, and Level 4, 4kV line-to-ground.

PART 2 The equipment shall be immune to electrical surges per ANSI/IEEE C62.41 Surge and Ring Wave.  Specified limits shall be 6kV line-to-line.

PART 2 The equipment shall be immune to radiated radio frequency emissions.  Specified limits shall be 10V/m at 150 MHz.

PART 2 Dielectric Isolation:  Equipment withstands an alternating current potential of 1000V plus twice the rated voltage of the equipment for 1 minute without breakdown between uninsulated live parts and the enclosure with the contacts open and closed; between terminals of opposite polarity with the contacts closed; and between uninsulated live parts of different circuits.
PART 2 Environmental Requirements

PART 2 The equipment shall operate continuously without derating in surrounding air temperatures of -40° to 70°C (-40° to 158°F).
PART 2 The equipment shall operate continuously without derating in relative humidity of 10% up to 95% non-condensing per IEC 68-2-3.
PART 2 The equipment shall operate properly after storage in ambient temperatures of -40° to 80°C (-40° to 176°F).

PART 2 Dimensions:  The equipment dimensions shall not exceed 1.750” H x 2.375” W x 4.125” D (with socket).

PART 2 Mounting:

PART 2 The equipment shall be mounted using the SymCom OT08-PC 8-pin octal socket.

a. The socket shall be 600V rated.

b. The socket shall be 10A rated.

c. The socket shall provide a means for mounting on the surface or on a DIN rail.

En SEQ CHAPTER \h \r 1d of Section
ES-201-SLD_A1  03/11/2010


[image: image1.png][image: image2.png][image: image3.png]